## Summary
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/22-23/00015/4
BILLS OF QUANTITIES GRAND SUMMARY
BILL No. | DESCRIPTION |  |  | TOTAL AMOUNT(Ushs)
GENERAL
1 | General Items |  |  | 44000000
2 | Dayworks |  |  | 0
WORKS ITEMS
3 | Tank 3 Community Supply Area
3.1 | Transmission 1: WTP to Tank 3 |  |  | 0
3.2 | 382m³ Tank 3 |  |  | 0
3.3 | Tank 3 Community Distribution Network & Service Connections |  |  | 0
| Total for Tank 3 Supply Area Carried to Collection |  |  | 0
4 | Tank 4 Community Supply Area
4.1 | Transmission 3: Tank 3 to Tank 4 |  |  | 0
4.2 | 296m³ Tank 4 |  |  | 0
4.3 | Tank 4 Community Distribution Network & Service Connections |  |  | 0
| Total for Tank 4 Supply Area Carried to Collection |  |  | 0
5 | Water Offices | No. | Rate
5.1 | Water Office Type 2 | 1 | 0 | 0
Total for Sanitation Infrastructure Carried to Collection |  |  |  | 0
6 | Sanitation Infrastructure | No. | Rate
6.1 | Institutional VIP for Gents | 1 | 0 | 0
6.2 | Institutional VIP for Ladies | 1 | 0 | 0
6.3 | Public Waterborne Toilet | 1 | 0 | 0
Total for Sanitation Infrastructure Carried to Collection |  |  |  | 0
7 | Environment and Social Safeguards |  |  | 0
Subtotal 1 |  |  |  | 44000000
ADD, 10% Contingencies |  |  |  | 4400000
Subtotal 2 |  |  |  | 48400000 | 12736.8421
ADD, 18% VAT |  |  |  | 8712000
GRAND TOTAL INCLUDING TAXES CARRIED TO BID FORM |  |  |  | 57112000

## B1 - General Items
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL NO. 1.0: GENERAL ITEMS
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
Contractual Requirements
A110 | Performance security | sum | 1 |  | 0
A120.1 | Insurance of the Works | sum | 1 |  | 0
A120.2 | Third party insurance | sum | 1 |  | 0
A120.3 | Insurance of Contractors Equipment | sum | 1 |  | 0
A120.4 | Workmen's Compensation | sum | 1 |  | 0
Services for the Project Manager's staff
Transport vehicles as specified
A221.1 | Provision of vehicles; Double Cabing Pickup | nr | 1 |  | 0
A221.2 | Maintenance of vehicles; Double Cabing Pickup upto 1000 km/month | Vehicle-month | 15 |  | 0
A221.3 | Maintenance of vehicles; Double Cabing Pickup over 1000 km/month | km | 10000 |  | 0
A221.4 | Provision of vehicles; 125CC off-road/ dirt mortor cycle (Clause 2.1.31) | nr | 1 |  | 0
A221.5 | Maintenance of vehicles; 125CC off-road/ dirt mortor cycle upto 1000 km/month x 2Nr. | Vehicle-month | 15 |  | 0
A221.6 | Maintenance of vehicles; 125CC off-road/ dirt mortor cycle over 1000 km/month x 2Nr. | km | 5000 |  | 0
Communication System
A222.1 | Establish communication system | sum | 1 |  | 0
A222.2 | Maintenance of the communication system | month | 15 |  | 0
Surveying Equipment
A233 | Provision of surveying equipment | month | 9 |  | 0
Attendance upon the Project Manager's staff
A241 | Provide services of drivers | month | 15 |  | 0
A242 | Provide services of chainmen | month | 9 |  | 0
A249.1 | Provide services of Secretary | month | 0 |  | 0
A249.2 | Provide services of Security Gaurd | month | 0 |  | 0
Testing of Materials
A250.1 | Pipes at Uganda Bureau of Standards | sum | 1 |  | 0
A250.2 | Concrete cubes at Ministry of Works Central Laboratories | nr | 25 |  | 0
Carried to Collection |  |  |  |  | 0
Testing of the Works
Pipeline pressure testing
A260.1 | Pressure testing of pipelines at joints per manufacturers specifications; ductile iron pipes, size not exceeding DN300mm; maximum test pressure not exceeding 32 bars. | km | 11.4 |  | 0
A260.2 | Pressure testing of pipelines; uPVC and HDPE; OD63 to OD280; maximum test pressure 20 bars | km | 44.5 |  | 0
A260.3 | Water Tightness testing of tanks | sum | 1 |  | 0
A260.4 | Testing and certification of mechanical and electrical systems | sum | 1 |  | 0
Temporary Works
A277 | De-watering; Allow for work in water affected areas, including all temporary works, pumping, protection, access, etc to ensure the works are completed as specified; include removal of facilities. | sum | 1 |  | 0
Site Sign Boards as follows
A279.1 | Establishment | nr | 2 |  | 0
A279.2 | Maintenance of site sign-boards until the issue of the Taking-Over of the Whole of the Works | wk | 72 |  | 0
A279.3 | Removal on completion | nr | 2 |  | 0
Surveys of Pipeline Routes as specified
A299.1 | Surveys and drawing production of pipeline routes; pipe diameter greater than 110mm | km | 55.9 |  | 0
Weather Records as specified
A299.3 | Weather Records | month | 15 |  | 0
Record Drawings
A299.4 | Production of As-Built Record drawings to Project Manager's approval | sum | 1 |  | 0
A299.5 | Production of Operating Manuals to Project Manager's approval | sum | 1 |  | 0
Carried to Collection |  |  |  |  | 0
Provisional Sums
A420.1 | Allow for relocation of existing services including repair of damage caused to all existing services (e.g. pipes, cables, drains, e.t.c) | Sum |  |  | 40000000
A999 | Contractor's charges and profits associated with administration of items A420.1 thru A420.10 (NOT TO EXCEED 10%) | % |  | 10% | 4000000
Carried to Collection |  |  |  |  | 44000000
Method-Related Charges
Method-related charges, if any, may be inserted by the Tenderer in accordance with Section 7 of CESMM4.
Fixed
A310 | Mobilisation on site | sum | 1 |  | 0
A311 | Demobilise on completion of the Works | sum | 1 |  | 0
A312 | Supply and/or erect Contractor's site offices, stores and workshop | sum | 1 |  | 0
A314 | Remove Contractor's site facilities on completion of the Works | sum | 1 |  | 0
Variable
A329 | Maintain Contractor's site offices, including all services | month | 15 |  | 0
A371 | Contractors Superintendance of Works | month | 15 |  | 0
Carried to Collection |  |  |  |  | 0
BILL NO. 1 - GENERAL ITEMS
Summary Page
| Page 1 of 4 |  |  |  | 0
| Page 2 of 4 |  |  |  | 0
| Page 3 of 4 |  |  |  | 44000000
| Page 4 of 4 |  |  |  | 0
Carried to Summary |  |  |  |  | 44000000

## B2 - DayWorks
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL NO. 2.0: DAY WORKS
ITEM NO. | DESCRIPTION | UNIT | QUANTITY | RATE(Ushs) | AMOUNT(Ushs)
Labour
DW 1.1 | Working ganger | hr | 30 |  | 0
DW 1.2 | Artisan | hr | 31 |  | 0
DW 1.3 | Semi-skilled | hr | 30 |  | 0
DW 1.4 | Unskilled | hr | 170 |  | 0
DW 1.5 | Driver for light vehicle | hr | 6 |  | 0
DW 1.6 | Driver for heavy vehicle | hr | 10 |  | 0
DW 1.7 | Operator for heavy equipment | hr | 15 |  | 0
Materials
DW 2.1 | Ordinary Portland Cement in 50 kg bags | t | 2 |  | 0
DW 2.2 | Coarse aggregate for concrete. | m³ | 1 |  | 0
DW 2.3 | Fine aggregate for concrete. | m³ | 3 |  | 0
DW 2.4 | Water for concrete | l | 10 |  | 0
DW 2.5 | Sand for building | m³ | 1 |  | 0
DW 2.6 | Sand for plaster | m³ | 1 |  | 0
DW 2.7 | Selected burnt clay bricks for building; size 230 x 115 x 115mm | nr | 997 |  | 0
DW 2.8 | Concrete blocks for building, 225 mm thick | m² | 1 |  | 0
DW 2.9 | Concrete blocks for building, 150 mm thick. | m² | 2 |  | 0
DW 2.10 | Hydrated lime for building | kg | 3 |  | 0
DW 2.11 | Timber, sawn. | m3 | 0.5 |  | 0
DW 2.12 | Timber wrot. | m3 | 0.5 |  | 0
High yield steel reinforcement:-
DW 2.13 | 8-10 mm dia | kg | 20 |  | 0
DW 2.14 | 12-16 mm dia. | kg | 10 |  | 0
DW 2.15 | 20-25 mm dia. | kg | 6 |  | 0
DW 2.16 | Steel reinforcement fabric reference:A193 | m² | 5 |  | 0
DW 2.17 | Steel reinforcement fabric reference:A252 | m² | 4 |  | 0
DW 2.18 | Hardcore filling | m³ | 2 |  | 0
DW 2.19 | Topsoil delivered to site | m³ | 1 |  | 0
Contractors Equipment
DW 3.1 | Road vehicles:Pick-up,1.5t. | hr | 5 |  | 0
Road vehicles:Lorries:
DW 3.2 | Flat - 5t capacity | hr | 5 |  | 0
DW 3.3 | Flat - 10t capacity | hr | 5 |  | 0
Tipping :
DW 3.4 | 5t capacity | hr | 5 |  | 0
DW 3.5 | 10t capacity | hr | 5 |  | 0
Water tankers with pump and hoses:
DW 3.6 | 2,500 litre capacity. | hr | 4 |  | 0
DW 3.7 | 5,000 litre capacity. | hr | 4 |  | 0
Carried to Collection |  |  |  |  | 0
Excavator, face shovel or dragline:
DW 3.8 | 0.25 m3 bucket. | hr | 5 |  | 0
DW 3.9 | 0.5m3 bucket. | hr | 4 |  | 0
DW 3.10 | 1.0m3 bucket. | hr | 3 |  | 0
DW 3.11 | excavator with a hydraulic hammer | hr | 5 |  | 0
Tractors:
DW 3.12 | rubber tyred with trailer, 75 kw. | hr | 0.5 |  | 0
DW 3.13 | tracked including bull and angle dozer with ripper:
| (i) 150 kw. | hr | 0.5 |  | 0
| (ii) 200 kw | hr | 0.5 |  | 0
| (iii) 250 kw. | hr | 0.5 |  | 0
Rollers:
DW 3.14 | manual, 250 kg | hr | 0.5 |  | 0
DW 3.15 | vibratory, self, propelled, 1500 kg. | hr | 0.5 |  | 0
Concrete mixers with weigh batchers and loading hoppers:
DW 3.16 | 300 litre capacity. | hr | 1 |  | 0
DW 3.17 | 400 litre capacity. | hr | 1 |  | 0
Concrete vibrator, pneumatic with hoses:
DW 3.18 | poker type, 50 mm | hr | 1 |  | 0
DW 3.19 | shutter type | hr | 1 |  | 0
Bar bending and shearing machines:
DW 3.20 | bending:-
| (1) hand operated. | hr | 2 |  | 0
| (2) power operated. | hr | 2 |  | 0
shearing:-
DW 3.21 | (1) hand operated | hr | 2 |  | 0
DW 3.22 | (2) power operated. | hr | 2 |  | 0
Air compressor, mobile with 5m hose and steels with:
DW 3.23 | 1 breker. | hr | 2 |  | 0
DW 3.24 | 2 breakers. | hr | 2 |  | 0
Dewatering Pumps with motor and 5m suction, 3m delivery hose
DW 3.25 | Norminal size 50mm. | hr | 20 |  | 0
DW 3.26 | Nominal size 100mm. | hr | 20 |  | 0
Mobile electricity generating sets, 240v, 1 ph, 50 Hz:
DW 3.27 | 5 kvA | hr | 5 |  | 0
DW 3.28 | 10 kvA | hr | 5 |  | 0
Carried to Collection |  |  |  |  | 0
COLLECTION
| Collection, Page 1 of 3 |  |  |  | 0
| Collection, Page 2 of 3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 3.1-Trans Tank 2 to Tank 3
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 3.1: Transmission 1: Junction Tank 2 to Tank 3
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe trench | ha | 8.4 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 6 |  | 0
Stumps
D310 | Diameter 150-500 mm | nr | 8 |  | 0
PIPEWORK-PIPES
Steel pipes PN10 to BS EN 525; spigot and socket joints
Not in trenches
I411 | DN150 | m | Rate Only |  | 0
I431 | DN300 support above ground | m | 40 |  | 0
In trenches depths as follows:
I422.1 | DN300 depth not exceeding 1.5m | m | 11071 |  | 0
I423 | DN300; depth 1.5 - 2m | m | 264 |  | 0
I422.2 | DN250 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.3 | DN200 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.3 | DN150 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.4 | DN100 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.5 | DN90 depth not exceeding 1.5m | m | Rate Only |  | 0
uPVC pressure pipes to UNBS US 264: 2000 and DIN 8062 with integral rubber ring socket joints laid in trenches depth not exceeding 1.5m
I522.1 | OD200 PN10 | m | Rate Only |  | 0
I522.2 | OD200 PN16 | m | Rate Only |  | 0
I522.3 | OD180 PN16 | m | Rate Only |  | 0
I522.4 | OD160 PN16 | m | Rate Only |  | 0
High density polyethylene pipes to UNBS US 482: 2003 and DIN 8074 laid in trench; depth not exceeding 1.5 m; rate to include selected excavated backfill
I712.1 | OD63 PN10 | m | Rate Only |  | 0
I712.2 | OD90 PN20 | m | Rate Only |  | 0
I712.3 | OD90 PN10 | m | Rate Only |  | 0
PIPEWORK-FITTINGS AND VALVES
Steel pipe fittings to BS EN 545; in trenches depth not exceeding 1.5 m
Bends
J311 | DN100 x 90o Duckfoot | nr | Rate Only |  | 0
Socketed bends
J312.1 | DN300 x 11.25o | nr | 4 |  | 0
J312.2 | DN300 x 22.5o | nr | 3 |  | 0
J313.1 | DN300 x 45o | nr | 3 |  | 0
J313.2 | DN300 x 90o | nr | 3 |  | 0
J311.1 | DN250 x 11.25o | nr | 0 |  | 0
Carried to Collection |  |  |  |  | 0
J311.2 | DN225 x 22.5o | nr | Rate Only |  | 0
J311.3 | DN225 x 45o | nr | Rate Only |  | 0
J311.4 | DN225 x 90o | nr | Rate Only |  | 0
J311.5 | DN200 x 22.5o | nr | Rate Only |  | 0
J311.6 | DN200 x 45o | nr | Rate Only |  | 0
J311.7 | DN200 x 90o | nr | Rate Only |  | 0
All flanged tees; flanges to PN16
J322.1 | DN300 x 200 | nr | 2 |  | 0
J322.2 | DN300 x 150 | nr | Rate Only |  | 0
J322.3 | DN300 x 90 | nr | Rate Only |  | 0
J322.4 | DN225 x 150 | nr | Rate Only |  | 0
Double socket tees with flanged branches; flanges to PN16
J322.5 | DN200 x 150 | nr | Rate Only |  | 0
J322.6 | DN180 x 125 | nr | Rate Only |  | 0
J322.7 | DN150 x 100 | nr | Rate Only |  | 0
J322.7 | DN150 x 90 | nr | Rate Only |  | 0
PIPEWORK-FITTINGS AND VALVES
Valves and Penstocks
Cast Iron gate valves to BS 5150 with PN 16 flanges to BS 4505; with T-key length not exceeding 1.5 m
J811 | DN100 | nr | 1 |  | 0
Cast iron butterfly valve to BS EN 593 with actuator and PN16 flanges to BS EN 1092; T-key operated
J843 | DN300 | nr | Rate Only |  | 0
J842 | DN225 | nr | Rate Only |  | 0
J861 | DN50 x 3-stage anti-surge anti-shock air valve as manufactured by Vent-o-Mat® complete with DN50 isolating valve | nr | 2 |  | 0
J871 | DN150 Pressure reducing Valve ; PN16 | nr | 1 |  | 0
J891 | DN100 Circular Flap Valve at washouts; PN16 flanges | nr | 9 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Concrete Chambers; depth not exceeding 1.5m
K231.1 | Washout chamber and cover complete | nr | 9 |  | 0
K231.4 | Airvalve chamber and cover complete | nr | 4 |  | 0
Stone-pitch lined trapezoidal ditches;
K492 | Cross-sectional area 1.5-2m2 | m | 20 |  | 0
K493 | Cross-sectional area 2-3m2 | m | 15 |  | 0
Crossings; pipe less than DN300
K652 | Brick and blockwork walls | nr | 8 |  | 0
K662 | Fences; barbed wire and chainlink | nr | 6 |  | 0
Breaking up, temporary and permanent reinstatement inclusive of processing the necessary approvals from the relevant authorities
K731.1 | Gravel roads; maximum pipe size DN300 | m | 28 |  | 0
K731.2 | Bitumen surfaced roads; maximum pipe size DN300 | m | 0 |  | 0
K742 | Concrete paving slab walkways including kerbstones | m | 15 |  | 0
Carried to Collection |  |  |  |  | 0
Reinstatement of land as directed by the Project Manager
K752.1 | Re-grassing | m | 50 |  | 0
K752.2 | Planting trees | nr | 14 |  | 0
K799 | Concrete-lined drains | m | 0 |  | 0
Marker posts as Dwg. ALA-ORA_SD_011
K820.1 | Marker posts | nr | 13 |  | 0
K820.2 | Pipe markers | nr | 3 |  | 0
K899.1 | Washout outfall structures complete as Dwg. ALA-ORA_SD_005 | nr | 9 |  | 0
PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to excavation and backfilling; excavation of rock
L111 | In pipe trenches | m3 | 685 |  | 0
L121 | In chambers | m3 | 4 |  | 0
Special pipe laying methods; pipe jacking/ horizontal directional drilling
L231 | Norminal bore DN300mm; for 1Nr. Road crossing. | m | 0 |  | 0
Surrounds as Dwg ALA-ORA_SD_010
L 5 3 4 | Imported granular material | m | 143 |  | 0
Class 20/20 mass concrete thrust blocks
L731 | Volume 0.2-0.5m3 | nr | 2 |  | 0
L741 | Volume 0.5-1m3 | nr | 4 |  | 0
L753.1 | Volume 1 - 2m3 | nr | 2 |  | 0
L751 | Volume 0.2-0.5m4 | nr | 3 |  | 0
Standard pipe supports in C25/20 reinforced concrete
Reinforced concrete pipe supports, class 25, as in drawing ALA-ORA_SD_011, complete including foudation bases, bolts and nuts, murram backfill, pipe diameter not exceeding 500mm and of the following heights above ground:-
L810 | Height not exceeding 1 m | nr | 6 |  | 0
L820 | Height 1- 1.5m | nr | Rate Only |  | 0
L830 | Height 1.5 - 2m | nr | Rate Only |  | 0
STRUCTURAL METALWORK
Fabrication and erection of rolled steel section pipe bridge including all earthworks, reinforced concrete abuttments and anchoraging complete as shown on drawings to the following spans.
M999.1 | Span not exceeding 10m | nr | Rate Only |  | 0
M999.2 | Span 10 -15m | nr | Rate Only |  | 0
M999.3 | Span 15 - 20m | nr | Rate Only |  | 0
M999.4 | Span 20 - 25m | nr | Rate Only |  | 0
M999.5 | Span 25 -30m | nr | Rate Only |  | 0
M999.6 | Span 30 - 35m | nr | 1 |  | 0
M999.7 | Span 35 - 40m | nr | Rate Only |  | 0
M999.8 | Span 40 - 50m | nr | Rate Only |  | 0
Carried to Collection |  |  |  |  | 0
TRANSMISSION MAIN
Summary Page
| Page 1 of 4 |  |  |  | 0
| Page 2 of 4 |  |  |  | 0
| Page 3 of 4 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 3.2 - Tank 3
MINISTRY OF WATER AND ENVIRONMENT
CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 3.2: 382m³ TANK
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
The relevant drawing is ENY_RSV_MVP_003 including references made there- in to other drawings
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for works | ha | 0.1 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 3 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E312 | Strip top soil, depth not exceeding 0.5 m and set aside for re-use | m³ | 56.4 |  | 0
Excavation for foundations; commencing surface is the stripped ground level
E323 | Depth 0.5 - 1 m | m³ | 56.4 |  | 0
E324 | Depth 1 - 2 m | m³ | 56.4 |  | 0
Excavation of rock; commencing surface is the stripped ground level
E334 | Depth 1 - 2 m | m³ | 6 |  | 0
Excavation Ancillaries
Disposal to satisfaction of Project Manager
| Topsoil | m³ | 45.12 |  | 0
E531 | Excavated Material | m³ | 22.56 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
E614 | To structures; selected excavated material | m³ | 33.84 |  | 0
E631 | General; excavated topsoil | m³ | 11.28 |  | 0
Landscaping
E810 | Preparation of the surfaces and planting of approved lawn grass | m² | 340 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Designed mix to BS EN 1992, with ordinary Portland cement to UNBS US 310:2002, aggregate to BS 882, for the following mixes
F122 | Strength C12/15, 20mm aggregate | m³ | 7.8 |  | 0
F141 | Strength C20/25, 10mm aggregate | m³ | 52.1 |  | 0
F172 | Strength C30/37, 10mm aggregate | m³ | 75.3 |  | 0
Placing Mass Concrete
Blinding
F611 | Thickness 75mm | m³ | 7.8 |  | 0
IN-SITU CONCRETE
Placing Reinforced Concrete
Bases
F722 | Concrete tank base; thickness 300mm | m³ | 7.8 |  | 0
F724 | Steel tank bases; thickness 500-750 mm | m³ | 52.1 |  | 0
Walls
F742 | Tank stub walls; thickness 250mm | m³ | 75.3 |  | 0
F743 | Concrete tank wall; thickness 350mm | m³ | 0 |  | 0
Carried to Collection |  |  |  |  | 0
Columns and piers
F752 | Concrete columns 0.09m2 cross-sectional area | m³ | 0 |  | 0
F754 | Tank support piers; 0.56m2 cross-section area | m³ | 0 |  | 0
CONCRETE ANCILLARIES
Formwork
G315 | Class S3; plane horizontal width exceeding 1.2m | m² | 0 |  | 0
G343 | Class S2 finish; Plane vertical width 0.3 m | m² | 336.3 |  | 0
For components of constant cross-section
Class S3 finish
G381 | Beams; 300 x 200mm wide | m | 0 |  | 0
G382.1 | Stub Columns; 500 x 500mm square | m | 0 |  | 0
G383.1 | Walls; 300mm thick | m | 0 |  | 0
Class S2 finish
G382.2 | Stub walls; 1.5m height; 250mm thick | m | 99 |  | 0
Reinforcement
G529 | High yield ribbed cold formed bars to BS EN 1992 and EN 10080; characteristic strength 500 MPa; nominal size 8 -16mm | t | 6.76 |  | 0
Joints
G621 | Sliding joint between wall and roof; width 0.35 m | m² | 0 |  | 0
G652 | Plastic waterstops of PVC to BS 903; width 300 mm | m | 0 |  | 0
Concrete Accessories
Finishing of top surfaces
G811 | Class U1 to steel tank bases | m² | 104 |  | 0
G813 | Class U3 to concrete tank floor, stub columns and stub walls | m² | 0 |  | 0
PIPEWORK - PIPES
Ductile iron pipe fittings to BS EN 545; PN16 flanges to BS 4504; cement mortar lined and epoxy coated
Not in trench
I321.1 | DN200 | m | 30 |  | 0
In trench depth not exceeding 1.5m
I322 | DN200 | m | 0 |  | 0
uPVC pressure pipes to BS 3505, with flexible joints to BS 4346 all to PN16, laid in trench to depth not exceeding 1.5m for the following pipe sizes
I512 | OD200 mm | m | 20 |  | 0
PIPEWORK - FITTINGS AND VALVES
Ductile iron pipe fittings to BS EN 545; PN16 flanges to BS 4504; cement mortar lined and epoxy coated
Flanged 90o bends
J311.1 | DN150 | nr | 1 |  | 0
J311.2 | DN200 | nr | 1 |  | 0
J312.1 | DN300 | nr | 1 |  | 0
J312.2 | DN350 | nr | 1 |  | 0
J311.3 | DN150 duckfoot | nr | 1 |  | 0
J311.4 | DN200 duckfoot | nr | 1 |  | 0
J312.3 | DN300 duckfoot | nr | 1 |  | 0
J312.4 | DN350 duckfoot | nr | 1 |  | 0
Flanged tees
J321 | DN350 x 200 | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
Tapers
J332 | DN250 x 200 | nr | 0 |  | 0
Detachable Coupling or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J341 | 150 mm ND | nr | 4 |  | 0
J342.1 | 200 mm ND | nr | 8 |  | 0
| 300 mm ND | nr | 4 |  | 0
Stepped couplings; DI to PVC
J351.1 | DN150/ OD160 | nr | 1 |  | 0
J351.2 | DN200/ OD225 | nr | 1 |  | 0
Flange Adaptors; maxi type
J351.3 | DN150 | nr | 1 |  | 0
J351.4 | DN200 | nr | 2 |  | 0
J352.2 | DN300 | nr | 1 |  | 0
J352.2 | DN350 | nr | 1 |  | 0
PIPEWORK - FITTINGS AND VALVES
Straight specials; double flanged pipe - pipe lengths to be confirmed BEFORE placing of orders
J381.1 | 150 mm ND, length not exceeding 0.2m Long | nr | 2 |  | 0
J381.2 | 150 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J381.3 | 150 mm ND, length not exceeding 6.0m Long | nr | 1 |  | 0
J382.1 | 200 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J382.2 | 200 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J382.3 | 200 mm ND, length not exceeding 6.0m Long | nr | 1 |  | 0
J382.4 | 300 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J382.5 | 300 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J382.6 | 300 mm ND, length not exceeding 6.0m Long | nr | 1 |  | 0
J382.7 | 350 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J382.8 | 350 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J382.9 | 350 mm ND, length not exceeding 6.0m Long | nr | 1 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491 | 200 mm ND | nr | 1 |  | 0
Cast Iron gate valves to BS 5150 with PN 16 flanges to BS 4505; hand operated
J811.1 | DN150 | nr | 1 |  | 0
J811.2 | DN200 | nr | 1 |  | 0
J812 | DN300 | nr | 1 |  | 0
0
Bulk Flow Meter complete with strainers
Woltman-type dry dial water meter as specified including pipe fittings, strainer and valves and as shown in drawings
J991.1 | DN150 | nr | 1 |  | 0
J991.2 | DN200 | nr | 1 |  | 0
Ball Float Valves
'Flanged Balanced ball float valve, flanges to BS4505, all to PN10
J891 | 200 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
In-situ Concrete chambers
Bulk meter chamber including cover and access
K231 | 2 x 2 x 1.5m deep | nr | 2 |  | 0
K231.3 | Washout Outfall structure as shown on drawings | nr | 1 |  | 0
K251 | Valve surface box for DN 100 - DN 300 valves, with lockable cover; depth not exceeding 1.5m | nr | 1 |  | 0
K453 | Grouted stone pitched lined rectangular section drain; cross section area 0.5-0.75m2 | m | 30 |  | 0
Carried to Collection |  |  |  |  | 0
MISCELLANEOUS METAL WORK
Cold Pressed Sectional Steel tanks of 1.22m plates to BS 1564 Type 2 complete with external flanges, cover and raised inlet, all as specified and as shown on drawings including internal pipe fittings. Support tower measured separately.
N287 | Tank capacity 382m3 (9 x 8 x 3 plates high) installed on 1m dwarf wall above ground | nr | 1 |  | 0
ROADS AND PAVINGS
Road Base and wearing course
Shape road surface and parking area by grading to camber and crossfall with a motor grader
R111 | Depth not exceeding 200 mm | m² | 120 |  | 0
Provide, transport up to site, spread, shape, stabilise and compact to atleast 95% MDD AASHTO approved gravel material for flexible base and wearing course, of the following thickness
R112 | Depth 250-300 mm | m3 | 45 |  | 0
Walkways
R912 | Concrete paved walkway; include sand bedding, earthworks and edge protection | m² | 20 |  | 0
MISCELLANEOUS WORKS
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 90 |  | 0
Gates
X235 | Metal vehicular access gate 3m wide complete with 1m side pedestrain entry gate all anchored in C25 reinforced concrete columns and pad foundations, painted to Project Manager's approval | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
COLLECTION
Summary Page
| Page 1 of 5 |  |  |  | 0
| Page 2 of 5 |  |  |  | 0
| Page 3 of 5 |  |  |  | 0
| Page 4 of 5 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 3.3- Tank3 Dist
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 3.3: Tank 3 Distribution Network & Service Connections
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
Preamble:
The quantities in this bill are mostly PROVISIONAL to be determined by the Project Manager on the basis of consumer demand
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | ha | 7.8 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 5 |  | 0
Stumps
D310 | Diameter 150-500 mm | nr | 5 |  | 0
D320 | Diameter 500 mm -1 m | nr | 3 |  | 0
PIPEWORK - PIPES
uPVC/HDPE pressure pipes to UNBS US 264: 2000 and DIN 8062 with integral rubber ring socket joints laid in trenches
OD 110 PN 10
I512.1 | Depth not exceeding 1.5m | m | 0 |  | 0
I513.1 | Depth 1.5-2m | m | 0 |  | 0
OD160 to PN 10
I512.2 | Depth not exceeding 1.5m | m | 1000 |  | 0
I513.2 | Depth 1.5-2m | m | 100 |  | 0
OD160 to PN 16
I512.3 | Depth not exceeding 1.5m | m | 5040 |  | 0
I513.3 | Depth 1.5-2m | m | 231 |  | 0
OD 200 PN 10
I522 | Depth not exceeding 1.5m | m | 3880 |  | 0
I523 | Depth 1.5-2m | m | 100 |  | 0
OD 250 PN 10
I532 | Depth not exceeding 1.5m | m | 2980 |  | 0
I533 | Depth 1.5-2m | m | 120 |  | 0
High density polyethylene pipes to UNBS US 482: 2003 and DIN 8074 laid in trench; depth not exceeding 1.5 m; rate to include selected excavated backfill
I712.1 | OD90, PN 16 | m | 0 |  | 0
I712.2 | OD90, PN 10 | m | 100 |  | 0
I712.3 | OD75, PN 10 | m | 100 |  | 0
I712.4 | OD63, PN 10 | m | 200 |  | 0
I712.5 | OD50, PN 10 | m | 300 |  | 0
I712.6 | OD40, PN 10 | m | 500 |  | 0
I712.7 | OD32, PN 10 | m | 500 |  | 0
I712.8 | OD25, PN 16, service pipes | m | 800 |  | 0
I712.9 | OD20, PN 16, service pipes | m | 20500 |  | 0
Carried to Collection |  |  |  |  | 0
PIPEWORK-FITTINGS AND VALVES
Steel pipe fittings; flanges to PN 16; in trenches not exceeding 1.5 m
Viking Johnson stepped couplings as Maxistep
J441.3 | DN100 x OD63 | nr | 1 |  | 0
J441.4 | DN100 x OD 75 | nr | 1 |  | 0
J441.5 | DN100 x OD100 | nr | 2 |  | 0
J441.6 | DN150 x OD100 | nr | 2 |  | 0
J441.7 | OD200 x OD 150 | nr | 0 |  | 0
Viking Johnson Flanged adaptors as Aquafast to PN10
J451.1 | OD75 | nr | 0 |  | 0
J451.2 | OD90 | nr | 0 |  | 0
J451.3 | OD110 | nr | 2 |  | 0
J451.4 | OD125 | nr | 1 |  | 0
J451.5 | OD160 | nr | 2 |  | 0
J451.6 | OD200 | nr | 2 |  | 0
End caps
J491.1 | OD110 | nr | 0 |  | 0
J491.2 | OD150 | nr | 5 |  | 0
PN 16 HDPE compression pipe fittings to DIN 8074/ BS 5114
Equal elbows
J611.1 | OD63 | nr | 1 |  | 0
J611.2 | OD50 | nr | 1 |  | 0
J611.3 | OD40 | nr | 1 |  | 0
J611.4 | OD32 | nr | 1 |  | 0
Equal tees
J621.1 | OD63 | nr | 1 |  | 0
J621.2 | OD50 | nr | 1 |  | 0
J621.3 | OD40 | nr | 1 |  | 0
J621.4 | OD32 | nr | 1 |  | 0
Reducing coupler
J631.1 | OD63 x 50 | nr | 2 |  | 0
J631.2 | OD50 x 40 | nr | 2 |  | 0
J631.3 | OD40 x 32 | nr | 3 |  | 0
J631.4 | OD32 x 25 | nr | 4 |  | 0
End caps
J691.1 | OD90 | nr | 2 |  | 0
J691.2 | OD75 | nr | 2 |  | 0
J691.3 | OD63 | nr | 2 |  | 0
J691.4 | OD50 | nr | 2 |  | 0
J691.5 | OD40 | nr | 4 |  | 0
J691.6 | OD32 | nr | 5 |  | 0
Valves and Penstocks
Cast Iron gate valves to BS EN 1171 with PN 16 flanges to BS 4505; with T-key length not exceeding 1.5 m
J811.1 | DN75 | nr | 0 |  | 0
J811.2 | DN90 | nr | 0 |  | 0
J811.3 | DN100 | nr | 2 |  | 0
J811.4 | DN125 | nr | 1 |  | 0
J811.5 | DN150 | nr | 1 |  | 0
J811.6 | DN200 | nr | 0 |  | 0
Circular Flap Valve to washouts; PN 10 flanges
J891.1 | DN100 | nr | 1 |  | 0
J891.2 | Fire hydrants to BS 750 Type 2 | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
In situ Concrete Chambers; depth not exceeding 1.5 m
K231.1 | Washout chamber as shown on drawings | nr | 2 |  | 0
K231.2 | Washout outfall structure as shown on drawings | nr | 2 |  | 0
K231.3 | Valve surface box as shown on drawings, complete | nr | 4 |  | 0
Stone-pitched trapezoidal ditches
K492 | Cross-sectional area 0.5 - 0.75 m2 | m | 10 |  | 0
K493 | Cross-sectional area 0.25 - 0.5 m2 | m | 8 |  | 0
Crossings; pipe not exceeding 300 mm
K611 | Streams; width 1 - 3 m | nr | 2 |  | 0
K641 | Hedges | nr | 4 |  | 0
K661 | Fences | nr | 4 |  | 0
Breaking up, temporary and permanent reinstatement; pipe not exceeding 300 mm
K731.1 | Gravel roads | m | 28 |  | 0
K731.2 | Double seal bitumen surfaced roads | m | 0 |  | 0
K799.1 | Mass concrete | m | 10 |  | 0
K799.2 | Stone-pitched lined drains | m | 0 |  | 0
Other pipework ancillaries
K820.1 | Marker Posts to Washouts | nr | 2 |  | 0
K820.2 | Pipe Marker Posts | nr | 4 |  | 0
Service connections
DN20 (½") connection to the following mains comprising saddle clamp and screwdown swivel ferrule with compression outlet for HDPE complete [PROVISIONAL ITEMS]
K861.1 | OD160 | nr | 40 |  | 0
K861.3 | OD125 | nr | 40 |  | 0
K861.4 | OD110 | nr | 40 |  | 0
K861.5 | OD90 | nr | 40 |  | 0
K861.6 | OD75 | nr | 40 |  | 0
K861.7 | OD63 | nr | 40 |  | 0
K861.8 | OD50 | nr | 40 |  | 0
DN25 (¾") connection to the following mains comprising saddle clamp and screwdown swivel ferrule with compression outlet for HDPE complete [PROVISIONAL ITEMS]
K861.10 | OD160 | nr | 20 |  | 0
K861.12 | OD125 | nr | 20 |  | 0
K861.13 | OD110 | nr | 20 |  | 0
K861.14 | OD90 | nr | 20 |  | 0
K861.15 | OD75 | nr | 20 |  | 0
K861.16 | OD63 | nr | 20 |  | 0
K861.17 | OD50 | nr | 10 |  | 0
Water supply installations as detailed on drawings
K899.1 | Yard Tap complete as drawing including galvanized iron pipe and fittings, brass stop cock, lockable tap and domestic water meter [PROVISIONAL ITEM] | nr | 410 |  | 0
K899.2 | Double tap Stand Post complete as drawing including galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, concrete headwall and slab with rock-filled soak-pit | nr | 8 |  | 0
Carried to Collection |  |  |  |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to excavation and backfilling
L111 | Excavation of rock in pipe trenches | m³ | 40 |  | 0
L118 | Excavation of natural material below Final Surface and backfilling with imported granular material in pipe trenches | m³ | 80 |  | 0
Surrounds; pipe not exceeding 200 mm
L531 | Imported granular material | m | 269 |  | 0
L541 | Mass concrete | m | 67 |  | 0
Mass Concrete C15 Thrust Blocks; pipe bore not exceeding 200mm
L721 | Volume 0.1 - 0.2 m³ | nr | 5 |  | 0
Steel pipe sleeves to PVC/HPDE pipes
L991.1 | DN125 pipe sleeve | m | 0 |  | 0
L991.2 | DN200 pipe sleeve | m | 10 |  | 0
STRUCTURAL METALWORK
Fabrication and erection of rolled steel section pipe bridge including all earthworks, reinforced concrete abuttments and anchoraging complete as shown on drawings to the following spans.
M999.1 | Span not exceeding 10m | nr | Rate Only |  | 0
M999.2 | Span 10 -15m | nr | Rate Only |  | 0
M999.3 | Span 15 - 20m | nr | Rate Only |  | 0
M999.4 | Span 20 - 25m | nr | Rate Only |  | 0
M999.5 | Span 25 -30m | nr | Rate Only |  | 0
M999.6 | Span 30 - 35m | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
PRIMARY DISTRIBUTION PIPEWORK
Summary Page
| Page 1 of 5 |  |  |  | 0
| Page 2 of 5 |  |  |  | 0
| Page 3 of 5 |  |  |  | 0
| Page 4 of 5 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 4.1- Trans to Tank 4
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 4.1: Transmission 3: Tank 3 to Tank 4
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe trench | ha | 4.4 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 6 |  | 0
Stumps
D310 | Diameter 150-500 mm | nr | 5 |  | 0
PIPEWORK-PIPES
Steel pipes PN10 to BS EN 525; spigot and socket joints
Not in trenches
I411 | DN150 | m | Rate Only |  | 0
I431 | DN300 support above ground | m | Rate Only |  | 0
In trenches depths as follows:
I422.1 | DN300 depth not exceeding 1.5m | m | Rate Only |  | 0
I423 | DN300; depth 1.5 - 2m | m | Rate Only |  | 0
I422.2 | DN250 depth not exceeding 1.5m | m | 3103 |  | 0
I422.3 | DN200 depth not exceeding 1.5m | m | 2346 |  | 0
I422.3 | DN150 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.4 | DN100 depth not exceeding 1.5m | m | Rate Only |  | 0
I422.5 | DN90 depth not exceeding 1.5m | m | Rate Only |  | 0
uPVC pressure pipes to UNBS US 264: 2000 and DIN 8062 with integral rubber ring socket joints laid in trenches depth not exceeding 1.5m
I522.1 | OD200 PN10 | m | Rate Only |  | 0
I522.2 | OD200 PN16 | m | Rate Only |  | 0
I522.3 | OD160 PN10 | m | 1883 |  | 0
I522.4 | OD160 PN16 | m | 6226 |  | 0
High density polyethylene pipes to UNBS US 482: 2003 and DIN 8074 laid in trench; depth not exceeding 1.5 m; rate to include selected excavated backfill
I712.1 | OD63 PN10 | m | Rate Only |  | 0
I712.2 | OD90 PN20 | m | Rate Only |  | 0
I712.3 | OD90 PN10 | m | Rate Only |  | 0
PIPEWORK-FITTINGS AND VALVES
Steel pipe fittings to BS EN 545; in trenches depth not exceeding 1.5 m
Bends
J311 | DN100 x 90o Duckfoot | nr | Rate Only |  | 0
Socketed bends
J312.1 | DN300 x 11.25o | nr | Rate Only |  | 0
J312.2 | DN300 x 22.5o | nr | Rate Only |  | 0
J313.1 | DN300 x 45o | nr | Rate Only |  | 0
J313.2 | DN300 x 90o | nr | Rate Only |  | 0
J311.1 | DN250 x 11.25o | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
J311.2 | DN250 x 22.5o | nr | 2 |  | 0
J311.3 | DN250 x 45o | nr | 2 |  | 0
J311.4 | DN250 x 90o | nr | 2 |  | 0
J311.5 | DN200 x 22.5o | nr | 2 |  | 0
J311.6 | DN200 x 45o | nr | 2 |  | 0
J311.7 | DN200 x 90o | nr | 2 |  | 0
All flanged tees; flanges to PN16
J322.1 | DN300 x 200 | nr | Rate Only |  | 0
J322.2 | DN300 x 150 | nr | Rate Only |  | 0
J322.3 | DN300 x 90 | nr | Rate Only |  | 0
J322.4 | DN250 x 150 | nr | 1 |  | 0
Double socket tees with flanged branches; flanges to PN16
J322.5 | DN200 x 150 | nr | 1 |  | 0
J322.6 | DN180 x 125 | nr | Rate Only |  | 0
J322.7 | DN150 x 100 | nr | Rate Only |  | 0
J322.7 | DN150 x 90 | nr | Rate Only |  | 0
PIPEWORK-FITTINGS AND VALVES
Valves and Penstocks
Cast Iron gate valves to BS 5150 with PN 16 flanges to BS 4505; with T-key length not exceeding 1.5 m
J811 | DN100 | nr | 2 |  | 0
Cast iron butterfly valve to BS EN 593 with actuator and PN16 flanges to BS EN 1092; T-key operated
J843 | DN300 | nr | 0 |  | 0
J842 | DN250 | nr | 1 |  | 0
J861 | DN50 x 3-stage anti-surge anti-shock air valve as manufactured by Vent-o-Mat® complete with DN50 isolating valve | nr | 2 |  | 0
J871 | DN150 Pressure reducing Valve ; PN16 | nr | 1 |  | 0
J891 | DN100 Circular Flap Valve at washouts; PN16 flanges | nr | 8 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Concrete Chambers; depth not exceeding 1.5m
K231.1 | Washout chamber and cover complete | nr | 8 |  | 0
K231.4 | Airvalve chamber and cover complete | nr | 5 |  | 0
Stone-pitch lined trapezoidal ditches;
K492 | Cross-sectional area 1.5-2m2 | m | 30 |  | 0
K493 | Cross-sectional area 2-3m2 | m | 20 |  | 0
Crossings; pipe less than DN300
K652 | Brick and blockwork walls | nr | 6 |  | 0
K662 | Fences; barbed wire and chainlink | nr | 5 |  | 0
Breaking up, temporary and permanent reinstatement inclusive of processing the necessary approvals from the relevant authorities
K731.1 | Gravel roads; maximum pipe size DN300 | m | 91 |  | 0
K731.2 | Bitumen surfaced roads; maximum pipe size DN300 | m | 8 |  | 0
K742 | Concrete paving slab walkways including kerbstones | m | 20 |  | 0
Carried to Collection |  |  |  |  | 0
Reinstatement of land as directed by the Project Manager
K752.1 | Re-grassing | m | 560 |  | 0
K752.2 | Planting trees | nr | 11 |  | 0
K799 | Concrete-lined drains | m | Rate Only |  | 0
Marker posts as Dwg. ALA-ORA_SD_011
K820.1 | Marker posts | nr | 13 |  | 0
K820.2 | Pipe markers | nr | 4 |  | 0
K899.1 | Washout outfall structures complete as Dwg. ALA-ORA_SD_005 | nr | 8 |  | 0
PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to excavation and backfilling; excavation of rock
L111 | In pipe trenches | m3 | 67 |  | 0
L121 | In chambers | m3 | 4 |  | 0
Special pipe laying methods; pipe jacking/ horizontal directional drilling
L231 | Norminal bore DN300mm; for 1Nr. Road crossing. | m | Rate Only |  | 0
Surrounds as Dwg ALA-ORA_SD_010
L 5 3 4 | Imported granular material | m | 112 |  | 0
Class 20/20 mass concrete thrust blocks
L731 | Volume 0.2-0.5m3 | nr | 2 |  | 0
L741 | Volume 0.5-1m3 | nr | 2 |  | 0
L753.1 | Volume 1 - 2m3 | nr | 2 |  | 0
Standard pipe supports in C25/20 reinforced concrete
Reinforced concrete pipe supports, class 25, as in drawing ALA-ORA_SD_011, complete including foudation bases, bolts and nuts, murram backfill, pipe diameter not exceeding 500mm and of the following heights above ground:-
L810 | Height not exceeding 1 m | nr | 6 |  | 0
L820 | Height 1- 1.5m | nr | Rate Only |  | 0
L830 | Height 1.5 - 2m | nr | Rate Only |  | 0
STRUCTURAL METALWORK
Fabrication and erection of rolled steel section pipe bridge including all earthworks, reinforced concrete abuttments and anchoraging complete as shown on drawings to the following spans.
M999.1 | Span not exceeding 10m | nr | Rate Only |  | 0
M999.2 | Span 10 -15m | nr | 1 |  | 0
M999.3 | Span 15 - 20m | nr | 1 |  | 0
M999.4 | Span 20 - 25m | nr | Rate Only |  | 0
M999.5 | Span 25 -30m | nr | Rate Only |  | 0
M999.6 | Span 30 - 35m | nr | Rate Only |  | 0
M999.7 | Span 35 - 40m | nr | Rate Only |  | 0
M999.8 | Span 40 - 50m | nr | Rate Only |  | 0
Carried to Collection |  |  |  |  | 0
TRANSMISSION MAIN
Summary Page
| Page 1 of 4 |  |  |  | 0
| Page 2 of 4 |  |  |  | 0
| Page 3 of 4 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 4.2 - Tank 4
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 4.2: 296m³ TANK 4
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
The relevant drawing is ENY_RSV_MVP_004 including references made there- in to other drawings
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for works | ha | 0.1 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 3 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E312 | Strip top soil, depth not exceeding 0.5 m and set aside for re-use | m³ | 37.5 |  | 0
Excavation for foundations; commencing surface is the stripped ground level
E323 | Depth 0.5 - 1 m | m³ | 52.1 |  | 0
E324 | Depth 1 - 2 m | m³ | 52.1 |  | 0
Excavation of rock; commencing surface is the stripped ground level
E334 | Depth 1 - 2 m | m³ | 3 |  | 0
Excavation Ancillaries
Disposal to satisfaction of Project Manager
| Topsoil | m³ | 30 |  | 0
E531 | Excavated Material | m³ | 20.84 |  | 0
E533 | Rock | m³ | 2 |  | 0
Filling
E614 | To structures; selected excavated material | m³ | 31.26 |  | 0
E631 | General; excavated topsoil | m³ | 7.5 |  | 0
Landscaping
E810 | Preparation of the surfaces and planting of approved lawn grass | m² | 400 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Designed mix to BS EN 1992, with ordinary Portland cement to UNBS US 310:2002, aggregate to BS 882, for the following mixes
F122 | Strength C12/15, 20mm aggregate | m³ | 7.8 |  | 0
F141 | Strength C20/25, 10mm aggregate | m³ | 52.1 |  | 0
F172 | Strength C30/37, 10mm aggregate | m³ | 15.7 |  | 0
Placing Mass Concrete
Blinding
F611 | Thickness 75mm | m³ | 7.8 |  | 0
IN-SITU CONCRETE
Placing Reinforced Concrete
Bases
F722 | Concrete tank base; thickness 300mm | m³ | 7.8 |  | 0
F724 | Steel tank bases; thickness 500-750 mm | m³ | 52.1 |  | 0
Walls
F742 | Tank stub walls; thickness 250mm | m³ | 15.7 |  | 0
F743 | Concrete tank wall; thickness 350mm | m³ | 0 |  | 0
Columns and piers
F752 | Concrete columns 0.09m2 cross-sectional area | m³ | 0 |  | 0
F754 | Tank support piers; 0.56m2 cross-section area | m³ | 0 |  | 0
Carried to Collection |  |  |  |  | 0
CONCRETE ANCILLARIES
Formwork
G315 | Class S3; plane horizontal width exceeding 1.2m | m² | 15 |  | 0
G343 | Class S2 finish; Plane vertical width 0.3 m | m² | 102.6 |  | 0
For components of constant cross-section
Class S3 finish
G381 | Beams; 300 x 200mm wide | m | 77 |  | 0
G382.1 | Stub Columns; 500 x 500mm square | m | 28.8 |  | 0
G383.1 | Walls; 300mm thick | m | 0 |  | 0
Class S2 finish
G382.2 | Stub walls; 1.5m height; 250mm thick | m | 0 |  | 0
Reinforcement
G529 | High yield ribbed cold formed bars to BS EN 1992 and EN 10080; characteristic strength 500 MPa; nominal size 8 -16mm | t | 3.78 |  | 0
Joints
G621 | Sliding joint between wall and roof; width 0.35 m | m² | 0 |  | 0
G652 | Plastic waterstops of PVC to BS 903; width 300 mm | m | 0 |  | 0
Concrete Accessories
Finishing of top surfaces
G811 | Class U1 to steel tank bases | m² | 103 |  | 0
G813 | Class U3 to concrete tank floor, stub columns and stub walls | m² | 0 |  | 0
PIPEWORK - PIPES
Ductile iron pipe fittings to BS EN 545; PN16 flanges to BS 4504; cement mortar lined and epoxy coated
Not in trench
I321.1 | DN200 | m | 30 |  | 0
In trench depth not exceeding 1.5m
I322 | DN200 | m | 20 |  | 0
uPVC pressure pipes to BS 3505, with flexible joints to BS 4346 all to PN16, laid in trench to depth not exceeding 1.5m for the following pipe sizes
I512 | OD200 mm | m | 20 |  | 0
uPVC drain pipes to BS 5481, with flexible joints to BS 4346 or BS 6209, laid in trench to depth not exceeding 1.5m for the following pipe sizes
I522 | OD300 mm | m | 0 |  | 0
PIPEWORK - FITTINGS AND VALVES
Ductile iron pipe fittings to BS EN 545; PN16 flanges to BS 4504; cement mortar lined and epoxy coated
Flanged 90o bends
J311.1 | DN150 | nr | 1 |  | 0
J311.2 | DN200 | nr | 1 |  | 0
J312.1 | DN250 | nr | 2 |  | 0
J311.3 | DN150 duckfoot | nr | 1 |  | 0
J311.4 | DN200 duckfoot | nr | 1 |  | 0
J312.2 | DN250 duckfoot | nr | 1 |  | 0
Detachable Coupling or similar, wide range coupling to fit all pipe spigots to PN 10, and of the following sizes
J342.1 | 150 mm ND | nr | 0 |  | 0
J342.2 | 200 mm ND | nr | 5 |  | 0
Carried to Collection |  |  |  |  | 0
Flanged tees
J321 | DN250 x 100 | nr | 1 |  | 0
Tapers
J332 | DN250 x 200 | nr | 0 |  | 0
Stepped couplings; DI to PVC
J351.1 | DN100/ OD110 | nr | 0 |  | 0
J351.2 | DN200/ OD225 | nr | 1 |  | 0
Flange Adaptors; maxi type
J351.3 | DN150 | nr | 1 |  | 0
J351.4 | DN200 | nr | 2 |  | 0
J352.2 | DN250 | nr | 0 |  | 0
Flanged bellmouth to ISO 2531, flanges to ISO 2441, of the following sizes all to PN 10
J372 | 250 mm ND | nr | 1 |  | 0
Straight specials; double flanged pipe - pipe lengths to be confirmed BEFORE placing of orders
J381.1 | 150 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J381.2 | 150 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J381.3 | 150 mm ND, length not exceeding 6.0m Long | nr | 2 |  | 0
J381.4 | 200 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J381.5 | 200 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J381.6 | 200 mm ND, length not exceeding 6.0m Long | nr | 2 |  | 0
J382.1 | 250 mm ND, length not exceeding 0.2m Long | nr | 1 |  | 0
J382.2 | 250 mm ND, length not exceeding 0.3m Long | nr | 1 |  | 0
J382.3 | 250 mm ND, length not exceeding 6.0m Long | nr | 1 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 10, cement mortar lined, and of the following sizes
J491 | 200 mm ND | nr | 1 |  | 0
Cast Iron gate valves to BS 5150 with PN 16 flanges to BS 4505; hand operated
J811.1 | DN100 | nr | 1 |  | 0
J811.2 | DN150 | nr | 1 |  | 0
J811.3 | DN200 | nr | 1 |  | 0
Bulk Flow Meter complete with strainers
Woltman-type dry dial water meter as specified including pipe fittings, strainer and valves and as shown in drawings
J991 | DN200 | nr | 1 |  | 0
Ball Float Valves
'Flanged Balanced ball float valve, flanges to BS4505, all to PN10
J891 | 150 mm ND | nr | 1 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK ANCILLARIES
In-situ Concrete chambers
Bulk meter chamber including cover and access
K231 | 2 x 2 x 1.5m deep | nr | 1 |  | 0
K231.3 | Washout Outfall structure as shown on drawings | nr | 1 |  | 0
K251 | Valve surface box for DN 100 - DN 300 valves, with lockable cover; depth not exceeding 1.5m | nr | 1 |  | 0
K453 | Grouted stone pitched lined rectangular section drain; cross section area 0.5-0.75m2 | m | 30 |  | 0
Carried to Collection |  |  |  |  | 0
MISCELLANEOUS WORKS
N199 | 12m structural steel support tower to match 296m3 tank supplied in Item N287 | sum | 1 |  | 0
Cold Pressed Sectional Steel tanks of 1.22m plates to BS 1564 Type 2 complete with external flanges, cover and raised inlet, all as specified and as shown on drawings including internal pipe fittings. Support tower measured separately.
N287 | Tank capacity 296m3 (8 x 7 x 3 plates high) installed on 12m tower above ground | nr | 1 |  | 0
ROADS AND PAVINGS
Road Base and wearing course
Shape road surface and parking area by grading to camber and crossfall with a motor grader
R111 | Depth not exceeding 200 mm | m² | 120 |  | 0
Provide, transport up to site, spread, shape, stabilise and compact to atleast 95% MDD AASHTO approved gravel material for flexible base and wearing course, of the following thickness
R112 | Depth 250-300 mm | m3 | 45 |  | 0
Walkways
R912 | Concrete paved walkway; include sand bedding, earthworks and edge protection | m² | 20 |  | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 90 |  | 0
Gates
X235 | Metal vehicular access gate 3m wide complete with 1m side pedestrain entry gate all anchored in C25 reinforced concrete columns and pad foundations, painted to Project Manager's approval | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
COLLECTION
Summary Page
| Page 1 of 5 |  |  |  | 0
| Page 2 of 5 |  |  |  | 0
| Page 3 of 5 |  |  |  | 0
| Page 4 of 5 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 4.3- Tank 4 Dist
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 4.3: Tank 4 Distribution Network & Service Connections
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
Preamble:
The quantities in this bill are mostly PROVISIONAL to be determined by the Project Manager on the basis of consumer demand
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | ha | 9.6 |  | 0
Trees
D210 | Girth 500 mm-1 m | nr | 8 |  | 0
Stumps
D310 | Diameter 150-500 mm | nr | 5 |  | 0
D320 | Diameter 500 mm -1 m | nr | 4 |  | 0
PIPEWORK - PIPES
uPVC/HDPE pressure pipes to UNBS US 264: 2000 and DIN 8062 with integral rubber ring socket joints laid in trenches
OD 110 PN 10
I512.1 | Depth not exceeding 1.5m | m | 5215 |  | 0
I513.1 | Depth 1.5-2m | m | 70 |  | 0
OD160 to PN 10
I512.2 | Depth not exceeding 1.5m | m | 3691 |  | 0
I513.2 | Depth 1.5-2m | m | 194 |  | 0
OD160 to PN 16
I512.3 | Depth not exceeding 1.5m | m | 4228 |  | 0
I513.3 | Depth 1.5-2m | m | 222 |  | 0
OD 200 PN 10
I522 | Depth not exceeding 1.5m | m | 2000 |  | 0
I523 | Depth 1.5-2m | m | 245 |  | 0
OD 250 PN 10
I532 | Depth not exceeding 1.5m | m | 0 |  | 0
I533 | Depth 1.5-2m | m | 0 |  | 0
High density polyethylene pipes to UNBS US 482: 2003 and DIN 8074 laid in trench; depth not exceeding 1.5 m; rate to include selected excavated backfill
I712.1 | OD90, PN 16 | m | Rate Only |  | 0
I712.2 | OD90, PN 10 | m | 100 |  | 0
I712.3 | OD75, PN 10 | m | 100 |  | 0
I712.4 | OD63, PN 10 | m | 200 |  | 0
I712.5 | OD50, PN 10 | m | 300 |  | 0
I712.6 | OD40, PN 10 | m | 500 |  | 0
I712.7 | OD32, PN 10 | m | 500 |  | 0
I712.8 | OD25, PN 16, service pipes | m | 800 |  | 0
I712.9 | OD20, PN 16, service pipes | m | 21000 |  | 0
Carried to Collection |  |  |  |  | 0
PIPEWORK-FITTINGS AND VALVES
Steel pipe fittings; flanges to PN 16; in trenches not exceeding 1.5 m
Viking Johnson stepped couplings as Maxistep
J441.3 | DN100 x OD63 | nr | 1 |  | 0
J441.4 | DN100 x OD 75 | nr | 1 |  | 0
J441.5 | DN100 x OD100 | nr | 2 |  | 0
J441.6 | DN150 x OD100 | nr | 4 |  | 0
J441.7 | OD200 x OD 150 | nr | Rate Only |  | 0
Viking Johnson Flanged adaptors as Aquafast to PN10
J451.1 | OD75 | nr | 2 |  | 0
J451.2 | OD90 | nr | 2 |  | 0
J451.3 | OD110 | nr | 2 |  | 0
J451.4 | OD125 | nr | 1 |  | 0
J451.5 | OD160 | nr | 2 |  | 0
J451.6 | OD200 | nr | 2 |  | 0
End caps
J491.1 | OD110 | nr | 3 |  | 0
J491.2 | OD150 | nr | 2 |  | 0
PN 16 HDPE compression pipe fittings to DIN 8074/ BS 5114
Equal elbows
J611.1 | OD63 | nr | 1 |  | 0
J611.2 | OD50 | nr | 1 |  | 0
J611.3 | OD40 | nr | 1 |  | 0
J611.4 | OD32 | nr | 1 |  | 0
Equal tees
J621.1 | OD63 | nr | 1 |  | 0
J621.2 | OD50 | nr | 1 |  | 0
J621.3 | OD40 | nr | 1 |  | 0
J621.4 | OD32 | nr | 1 |  | 0
Reducing coupler
J631.1 | OD63 x 50 | nr | 2 |  | 0
J631.2 | OD50 x 40 | nr | 2 |  | 0
J631.3 | OD40 x 32 | nr | 3 |  | 0
J631.4 | OD32 x 25 | nr | 4 |  | 0
End caps
J691.1 | OD90 | nr | 2 |  | 0
J691.2 | OD75 | nr | 2 |  | 0
J691.3 | OD63 | nr | 2 |  | 0
J691.4 | OD50 | nr | 2 |  | 0
J691.5 | OD40 | nr | 4 |  | 0
J691.6 | OD32 | nr | 5 |  | 0
Valves and Penstocks
Cast Iron gate valves to BS EN 1171 with PN 16 flanges to BS 4505; with T-key length not exceeding 1.5 m
J811.1 | DN75 | nr | 1 |  | 0
J811.2 | DN90 | nr | 1 |  | 0
J811.3 | DN100 | nr | 2 |  | 0
J811.4 | DN125 | nr | 1 |  | 0
J811.5 | DN150 | nr | Rate Only |  | 0
J811.6 | DN200 | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
Circular Flap Valve to washouts; PN 10 flanges
J891.1 | DN100 | nr | 2 |  | 0
J891.2 | Fire hydrants to BS 750 Type 2 | nr | Rate Only |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
In situ Concrete Chambers; depth not exceeding 1.5 m
K231.1 | Washout chamber as shown on drawings | nr | 2 |  | 0
K231.2 | Washout outfall structure as shown on drawings | nr | 2 |  | 0
K231.3 | Valve surface box as shown on drawings, complete | nr | 7 |  | 0
Stone-pitched trapezoidal ditches
K492 | Cross-sectional area 0.5 - 0.75 m2 | m | 10 |  | 0
K493 | Cross-sectional area 0.25 - 0.5 m2 | m | 5 |  | 0
Crossings; pipe not exceeding 300 mm
K611 | Streams; width 1 - 3 m | nr | 1 |  | 0
K641 | Hedges | nr | 5 |  | 0
K661 | Fences | nr | 5 |  | 0
Breaking up, temporary and permanent reinstatement; pipe not exceeding 300 mm
K731.1 | Gravel roads | m | 48 |  | 0
K731.2 | Double seal bitumen surfaced roads | m | Rate Only |  | 0
K799.1 | Mass concrete | m | 20 |  | 0
K799.2 | Stone-pitched lined drains | m | Rate Only |  | 0
Other pipework ancillaries
K820.1 | Marker Posts to Washouts | nr | 2 |  | 0
K820.2 | Pipe Marker Posts | nr | 4 |  | 0
Service connections
DN20 (½") connection to the following mains comprising saddle clamp and screwdown swivel ferrule with compression outlet for HDPE complete [PROVISIONAL ITEMS]
K861.1 | OD160 | nr | 40 |  | 0
K861.3 | OD125 | nr | 40 |  | 0
K861.4 | OD110 | nr | 40 |  | 0
K861.5 | OD90 | nr | 40 |  | 0
K861.6 | OD75 | nr | 40 |  | 0
K861.7 | OD63 | nr | 40 |  | 0
K861.8 | OD50 | nr | 40 |  | 0
DN25 (¾") connection to the following mains comprising saddle clamp and screwdown swivel ferrule with compression outlet for HDPE complete [PROVISIONAL ITEMS]
K861.10 | OD160 | nr | 30 |  | 0
K861.12 | OD125 | nr | 20 |  | 0
K861.13 | OD110 | nr | 20 |  | 0
K861.14 | OD90 | nr | 20 |  | 0
K861.15 | OD75 | nr | 20 |  | 0
K861.16 | OD63 | nr | 20 |  | 0
K861.17 | OD50 | nr | 10 |  | 0
Carried to Collection |  |  |  |  | 0
Water supply installations as detailed on drawings
K899.1 | Yard Tap complete as drawing including galvanized iron pipe and fittings, brass stop cock, lockable tap and domestic water meter [PROVISIONAL ITEM] | nr | 420 |  | 0
K899.2 | Double tap Stand Post complete as drawing including galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, concrete headwall and slab with rock-filled soak-pit | nr | 8 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to excavation and backfilling
L111 | Excavation of rock in pipe trenches | m³ | 50 |  | 0
L118 | Excavation of natural material below Final Surface and backfilling with imported granular material in pipe trenches | m³ | 100 |  | 0
Surrounds; pipe not exceeding 200 mm
L531 | Imported granular material | m | 321 |  | 0
L541 | Mass concrete | m | 80 |  | 0
Mass Concrete C15 Thrust Blocks; pipe bore not exceeding 200mm
L721 | Volume 0.1 - 0.2 m³ | nr | 6 |  | 0
Steel pipe sleeves to PVC/HPDE pipes
L991.1 | DN125 pipe sleeve | m | Rate Only |  | 0
L991.2 | DN200 pipe sleeve | m | 30 |  | 0
Carried to Collection |  |  |  |  | 0
PRIMARY DISTRIBUTION PIPEWORK
Summary Page
| Page 1 of 4 |  |  |  | 0
| Page 2 of 4 |  |  |  | 0
| Page 3 of 4 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Bill 5 - Water Office Type 2
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 5: WATER OFFICE BLOCK - Type 2
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
Preamble:
The works under this bill are covered under the Particular Specifications.
The relevant drawing is ALA-ORA-SD-016B including references made there- in to other drawings
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for office premises | m2 | 65 |  | 0
Trees
Cut and dispose of trees of the following girths; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
D220 | Girth 1-2 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 m for site | m³ | 10 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material,commencing surface is the formation level
E322 | Depth 0.25-0.5m | m³ | 10 |  | 0
E323 | Depth 0.5-1m | m³ | 20 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5 - 1.0 m | m³ | 2 |  | 0
Excavation Ancillaries
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 27.6 |  | 0
Carried to Collection |  |  |  |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 1 |  | 0
Disposal of Excavated Material
Disposal of excavated material to fill sites as specified and as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 16.6667 |  | 0
E533 | Rock | m³ | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to office area and compacted to 98% MOD AASHTO | m³ | 14 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 1.725 |  | 0
E647 | 300mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 7.2 |  | 0
Trimming
Trimming of surfaces filled with material other than topsoil, rock or artificial hard material, for the following types of work surfaces
E712 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
Trimming of surfaces filled with rock for the following types of work surfaces
E713 | Surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 1 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 200 |  | 0
Carried to Collection |  |  |  |  | 0
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F132 | 20mm aggregate | m³ | 3 |  | 0
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F142 | 20mm aggregate | m³ | 10 |  | 0
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F622 | Thickness 150-300mm | m³ | 3 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab of the following thickness
F622 | Thickness 150-300mm | m³ | 10 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F762 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to office block of the following width
G213 | Width 0.2 - 0.4m | m² | 5 |  | 0
G214 | Width 0.4 - 1.22m | m² | 0 |  | 0
Carried to Collection |  |  |  |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G241 | Width not exceeding 0.15m | m² | 5 |  | 0
G243 | Width 0.2 - 0.4m | m² | 25 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 100 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m² | 45 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of office block | m2 | 45 |  | 0
G812 | Steel float finish | m2 | 0 |  | 0
ROADS AND PAVINGS
Road Base and Wearing Course
Shape road surface and parking area by medium grading to camber and crossfall with a motor grader
R111 | Depth not exceeding 200 mm | m² | 150 |  | 0
Provide, transport up to site, spread, shape, stabilise and compact to atleast 95% MDD AASHTO approved gravel material for flexible base and wearing course, of the following thickness
R112 | Depth 150-300 mm | m3 | 60 |  | 0
Kerbs
Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment
R711 | Straight or curved to a radius exceeding 12 m | m | 40 |  | 0
R712 | To a radius not exceeding 12 m | m | 15 |  | 0
Carried to Collection |  |  |  |  | 0
Walkways
R911 | Concrete (C20) paved walkway in 600 x 600 x 50mm thick sections; include sand bedding, earthworks, jointing and concrete edge protection | m² | 40 |  | 0
BRICKWORK & MASONRY
Dense concrete blockwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete, as detailed in the drawings, for walls of the following thickness
U521.1 | 150 mm thick | m2 | 113 |  | 0
U521.2 | 230 mm thick | m2 | 40 |  | 0
Permanent Vents
Fired clay vent bricks to BS 7263, jointed with ordinary 1:5 cement mortar above door and window openings, including plastic gauze mosquito mesh sandwiched on a GI coffee tray mesh, for walls of the following thickness
U589 | 150 - 230 mm thick | m2 | 0.66 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 8 |  | 0
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 57 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 116 |  | 0
WATER PROOFING
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
W113 | 230 mm wide | m | 50 |  | 0
Carried to Collection |  |  |  |  | 0
Rendering
W153 | Surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m² | 57 |  | 0
Roofing
W322 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, Kiln fired clay roofing tiles; including ridge caps for pitched trussed roof. and 112mm uPVC rain water guttering and DN 80 drainage pipes to the Engineer's satisfaction. | m2 | 73 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 40 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 150 - 230 mm thick | m | 50 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 40 |  | 0
MISCELLANEOUS WORKS
Fences
X135 | Concrete post and chainlink wire fence complete as shown on drawings; height 2 - 2.5 m | m | 90 |  | 0
Gates
X235 | Metal field gate; width 3 - 4 m double leaf with personnel-access gate 1.0m wide | nr | 1 |  | 0
X399 | Drain to splash apron around building as specified and shown on drawings | m | 40 |  | 0
Site Works
X999.1 | Water supply connection to the Office block | sum | 1 |  | 0
X999.2 | Sanitary drainage system comprising in situ concrete manholes, OD160 PVC drain pipes, in situ concrete septic tank including manhole covers together with rock-filled soak-pit all as detailed on the drawings | sum | 1 |  | 0
Carried to Collection |  |  |  |  | 0
SIMPLE BUILDING WORKS INCIDENTAL TO CIVIL ENGINEERING WORKS
Z119 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600 x 600mm hardwood access trap door | m² | 63 |  | 0
Windows, doors and glazing
Timber solid panel hardwood doors include frame, all ironmongery, varnishing and locking arrangements with a permanent vent of 200mm
Z313.1 | Single leaf size 2.4 x 0.9m | nr | 2 |  | 0
Z313.2 | Double leaf size 2.4 x 0.8m wide | nr | 0 |  | 0
Steel frame glazed window include frame, burglar proofing, glazing and all iron mongery with louvered permanent vent of 200mm as follows
Z321.1 | Casement window 1.2m x 1.2m clear opening | nr | 2 |  | 0
Z321.2 | Casement window 0.6 x 0.8m clear opening | nr | 3 |  | 0
Z321.3 | Mild steel permanent vent overall size 800mm x 300mm high comprising 50 x 50 x 2mm angle section steel framing and 75 x 2mm thick mild steel louvres welded to frame | nr | 2 |  | 0
Single leaf steel casement door including frame, burglar proofing, glazing and all iron mongery and locks with louvered permanent vent of 200mm
Z323.1 | Door 2.4 x 1.5m wide clear opening; full glazing | nr | 1 |  | 0
Z323.1 | Door 2.4 x 1.2m wide clear opening; full glazing | nr | 0 |  | 0
Z323.2 | Door 2.4 x 0.9m wide; half steel plate and half glazed | nr | 2 |  | 0
0
Surface finishes
Cement plaster
Z413 | To walls | m² | 80 |  | 0
Z414 | To ceiling and eaves soffit on expanded metal and timber frame including cornices | m2 | 63 |  | 0
Tiles
Z421 | Floor tiles to washrooms | m2 | 9 |  | 0
Z423 | Walls tiles in washrooms | m2 | 42 |  | 0
Piped building services
Z519.1 | Water supply to all sanitary appliances and fittings within building including pipes and fittings | sum | 1 |  | 0
Z519.2 | Washwater drainage system from all sanitary appliances and fittings complete to first manhole including vent pipes | sum | 1 |  | 0
Z539.1 | Wash hand basin complete | nr | 2 |  | 0
Z539.2 | Water Closet complete | nr | 2 |  | 0
Z539.3 | Urinal | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
Cabled building servcies
Z799.1 | Electrical distribution system within building complete including lights, sockets, switches, fittings, fixtures and miniature circuit breakers | sum | 1 |  | 0
Z799.2 | Electrical earthing system to building | sum | 1 |  | 0
Supply of Office Furniture and Equipment
Z999 | Office Furniture and Equipment as Particular Specification Clause 2.1.31 (items to be handed over at Taking-Over of the Completed Works) | sum | 1 |  | 0
Electrical Installations
ME01 | 1000W 12V solar generator system comprising 6x100W 12V solar panels as DAYLIFF Cat. No. YL100, 630A charge controller, 5x200Ah 12V solar battery and 16000W 240V AC inverter complete with protection and indicating facilities and all accessories. | System | 1 |  | 0
ME02 | 100A 6way SPN MCB consumer unit complete with integral isolator and 2No. 32A and 4No6A MCBs | No. | 1 |  | 0
ME03 | Wire socket outlets in 3x2.5mm2 PVC insulated copper cables in concealed PVC conduit | No. | 8 |  | 0
ME04 | Wire lighting points through 6A switches in 3x1.5mm2 PVC insulated copper cables in concealed PVC conduit | No | 12
Fittings
ME05 | Pendant lighting fitting comprising ceiling rose 300mm 3x1.mm2 flexible copper cable, lamp holder and 6W LED lamp | No | 5 |  | 0
ME06 | 13A 2gang switched socket outlet | No | 6 |  | 0
ME07 | Earth the 1No. 2bedroom Block to the requirements of BS 7671 | Item | 1 |  | 0
ME08 | Lightning protection for the block in 1No air terminal 40metres 3x25mm copper tape including clips, 2No inspection claps and 16mm diameter 1.5m long copper rod buried in 300mmx300 mmx1.5mdeep earth | Item | 1 |  | 0
ME09 | Allow for testing the electrical installations at the block | Item | 1 |  | 0
Carried to Collection |  |  |  |  | 0
Collection
| Collection, Page 1/9 |  |  |  | 0
| Collection, Page 2/9 |  |  |  | 0
| Collection, Page 3/9 |  |  |  | 0
| Collection, Page 4/9 |  |  |  | 0
| Collection, Page 5/9 |  |  |  | 0
| Collection, Page 6/9 |  |  |  | 0
| Collection, Page 7/9 |  |  |  | 0
| Collection, Page 8/9 |  |  |  | 0
Total Cost of Office Blocks Carried to Summary |  |  |  |  | 0

## Bill 6.1 - SAN BOYS
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 6.1: 4 -STANCE LINED VIP INSTITUTIONAL TOILET- BOYS
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
The works under this bill are covered under the Particular Specifications. The relevant drawings are the DRAWING ALA-ORA_SAN_001, series (including references made there-in to other drawings)
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | ha | 0.008 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 2 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 2 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 8 |  | 0
E324 | Depth 1 - 2 m | m³ | 1 |  | 0
E325 | Depth 2 - 5 m | m³ | 65 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 53.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 79.8 |  | 0
E533 | Rock | m³ | 3 |  | 0
Carried to Collection |  |  |  |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 23.5 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F231 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F241 | 10mm aggregate | m³ | 10.3 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for slab footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault and ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
Placing mass concrete C25, for ground slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 2 |  | 0
Placing Reinforced Concrete
Bases, Footings and Slabs
Placing reinforced concrete C25, for suspended slab and footings of the following thickness
F622 | Thickness 150-300mm | m³ | 3.6 |  | 0
Beams
Placing reinforced concrete, grade C25, for beams of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1 |  | 0
Carried to Collection |  |  |  |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 48.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 48.5 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 230 mm thick | m² | 77 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 35 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 5 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 28 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6 |  | 0
Carried to Collection |  |  |  |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 75 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 187 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 12 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 30.5 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
X599.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 5 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
X599.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
X599.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
X599.4 | Supply and complete installation of corrosion proof manhole access covers 500mm x 650mm complete as specified including lifting hooks | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
Roofing
X599.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 45 |  | 0
Building Finishes
X599.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
X599.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
X599.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
X599.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
X599.10 | Supply and fix squating satopans in all stances | nr | 5 |  | 0
X599.11 | Supply and fix seating satopan in the disabled | nr | 1 |  | 0
Water and Drainage
X599.12 | Construct Urinal facility complete with floor trap, domical removable cast iron grating, gulley trap and including OD 110 uPVC PN 6 drainage pipework to soak away pit | sum | 1 |  | 0
X599.13 | SUPPLY AND FIX Washalots comprising 3m long x 110mm diameter BLUE HDPE pipe; 3No. 110 x 170 x 6mm PE plate; 10No. stainless steel outlet with strainer at 300mm centers; 3No. 50mm diameter GI stand pipe with metal lugs cast into mass concrete C20 (20mm aggregate) including soap holder; 3No. 150mm dia x 5mm stainless steel flexible clamps; allow for all the neccessary fixing accessories (Prices should include connection to the water supply system with 20mm HDPE pipe complete with all accessories) | nr | 2 |  | 0
X599.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
X599.15 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
Electrical Installation
X599.16 | Allow for electric power connection to the toilet block limited to MK boxes and bulb holders | sum | 0 |  | 0
X599.17 | Supply and Install 3No. security lights with all respective electricals; i.e. MCB, copper cables, earthing protection,etc, complete with all accessories as specified and directed by the Engineer | sum | 0 |  | 0
Carried to Collection |  |  |  |  | 0
Summary Page
| Page 1 of 6 |  |  |  | 0
| Page 2 of 6 |  |  |  | 0
| Page 3 of 6 |  |  |  | 0
| Page 4 of 6 |  |  |  | 0
| Page 5 of 6 |  |  |  | 0
Carried to Grand Summary |  |  |  |  | 0

## Bill 6.2 - SAN GIRLS
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 6.2: INSTITUTIONAL VIP FOR TOILET- LADIES
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
Preamble:
The works under this bill are covered under the Particular Specifications. The relevant drawings are the DRAWING ALA-ORA_SAN_002, series (including references made there-in to other drawings)
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | ha | 0.007 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 9.45 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 2 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 4 |  | 0
E324 | Depth 1 - 2 m | m³ | 18 |  | 0
E325 | Depth 2 - 5 m | m³ | 20.5 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 1 |  | 0
E334 | Depth 1 - 2 m | m³ | 1 |  | 0
E335 | Depth 2 - 5 m | m³ | 1 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 48 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6.5 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 34.5 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 6 |  | 0
Carried to Collection |  |  |  |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 38.5 |  | 0
E533 | Rock | m³ | 3 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 4.8 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 3.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 48.5 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F122 | 10mm aggregate | m³ | 0.5 |  | 0
Grade C20
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F132 | 10mm aggregate | m³ |  |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F142 | 10mm aggregate | m³ | 12.4 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for slab footings, grade C15, of the following thickness
F511 | Thickness not exceeding 150mm | m³ | 0.5 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for vault and ground slab of the following thickness
F522.1 | Thickness 150-300mm | m³ | 3.7 |  | 0
Placing mass concrete C20, for suspended slab and ramp base of the following thickness
F522.2 | Thickness 150-300mm | m³ | 5 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C25, for footings of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Carried to Collection |  |  |  |  | 0
Beams
Placing reinforced concrete, grade C25, for beams of the following cross-sectional area
F762 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 2 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 1.3 |  | 0
G215 | Width exceeding 1.22m | m² | 13.5 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244 | Width 0.4 - 1.22m | m² | 46.7 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.26 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 21.5 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 21.5 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U111.1 | 200 mm thick | m² | 87 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U111.2 | 150 mm thick | m² | 48 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U111.3 | 100 mm thick | m² | 5 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7 |  | 0
Carried to Collection |  |  |  |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 52 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 85 |  | 0
WATER PROOFING
Damp Proofing
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
W113 | 200 mm wide | m | 40 |  | 0
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 58.3 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 49 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 11 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 18 |  | 0
MISCELLANEOUS WORKS
Structural
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
X599.1 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 6 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
X599.2 | Single leaf door overall size 1000 x 2100mm high | nr | 1 |  | 0
Vault Access Slabs
Supply and Install pre-fabricated concrete slabs 120mm thick, inclusive of the squat pit and leg placements and of the following dimensions
X599.3 | 1200mm x 1400mm (W x L) | nr | 5 |  | 0
X599.4 | Supply and complete installation of corrosion proof manhole access covers 500mm x 650mm complete as specified including lifting hooks | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
Roofing
X599.5 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 18.4 |  | 0
Building Finishes
X599.6 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail | sum | 1 |  | 0
X599.7 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 2 |  | 0
X599.8 | Supply and Install OD 110 mm uPVC PN 6 vent pipe, complete with Tee, wire gauze fly screens and all ancillaries | m | 25 |  | 0
X599.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 5no. toilet paper holders, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
X599.10 | Supply and fix squating satopans in all stances | nr | 5 |  | 0
X599.11 | Supply and fix seating satopan in the disabled | nr | 1 |  | 0
Water and Drainage
X599.12 | Construct Urinal facility complete with floor trap, domical removable cast iron grating, gulley trap and including OD 110 uPVC PN 6 drainage pipework to soak away pit | sum | 1 |  | 0
X599.13 | SUPPLY AND FIX Washalots comprising 3m long x 110mm diameter BLUE HDPE pipe; 3No. 110 x 170 x 6mm PE plate; 10No. stainless steel outlet with strainer at 300mm centers; 3No. 50mm diameter GI stand pipe with metal lugs cast into mass concrete C20 (20mm aggregate) including soap holder; 3No. 150mm dia x 5mm stainless steel flexible clamps; allow for all the neccessary fixing accessories (Prices should include connection to the water supply system with 20mm HDPE pipe complete with all accessories) | nr | 2 |  | 0
X599.14 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
X599.15 | Supply and place pre-painted smooth wooden squat covers complete with lifting handles to the approval of the engineer | nr | 5 |  | 0
PROVISIONAL SUMS
Electrical Installation
X599.16 | Allow for electric power connection to the toilet block including processing a customer account with UMEME | sum | Rate Only |  | 0
X599.17 | Supply and Install 3No. security lights with all respective electricals; i.e. MCB, copper cables, earthing protection,etc, complete with all accessories as specified and directed by the Engineer | sum | Rate Only |  | 0
X599.18 | Allow for construction of an incinerator attached to the toilet, complete with a Chimney, access doors, steel grating, all as shown in the drawings and as directed by the Engineer. Include appropriate fireproofing and insulation to protect combustible elements of the building | sum | Rate Only |  | 0
X599.19 | Allow for profits and overheads on Item No. Electrical Installation | % | Rate Only |  | 0
Carried to Collection |  |  |  |  | 0
Summary Page
| Page 1 of 6 |  |  |  | 0
| Page 2 of 6 |  |  |  | 0
| Page 3 of 6 |  |  |  | 0
| Page 4 of 6 |  |  |  | 0
| Page 5 of 6 |  |  |  | 0
Carried to Grand Summary |  |  |  |  | 0

## Bill 6.3 - PUBLIC TOILET
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/…..
BILL No. 6.3: WATERBORNE PUBLIC TOILET
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
The works under this bill are covered under the Particular Specifications. The relevant drawings are the DRAWING ALA-ORA_SAN_003, series (including references made there-in to other drawings)
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for toilet | ha | 0.0154 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 1 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 1 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip top soil, depth not exceeding 0.15 for toilet foundation | m³ | 23.1 |  | 0
Ordinary Soil
Excavation for foundations in material other than topsoil,rock or artificial hard material, commencing surface is the formation level
E322 | Depth not exceeding 0.5m | m³ | 1.4 |  | 0
E323 | Depth 0.5 - 1 m | m³ | 18.9 |  | 0
E324 | Depth 1 - 2 m | m³ | 24.5 |  | 0
Rock
Excavation for foundations in rock,commencing surface is the exposed surface of the rock
E333 | Depth 0.5-1m | m³ | 0.7 |  | 0
E334 | Depth 1 - 2 m | m³ | 0.7 |  | 0
Excavation Ancillaries
Trimming
Trimming of excavated surfaces for whole structure in the following materials
E512 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 60.2 |  | 0
E513 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 4.6 |  | 0
Preparation
Preparation of excavated surfaces for whole structure in the following materials
E522 | Material other than topsoil,rock,or artificial hard material inclined at an angle not exceeding 45 degrees to the horizontal | m² | 104.3 |  | 0
E523 | Rock surfaces inclined at an angle not exceeding 45 degrees to the horizontal | m² | 4.2 |  | 0
Carried to Collection |  |  |  |  | 0
Disposal of Excavated Material
Disposal of excavated material to approved sites as directed by the Engineer
E532 | Material other than topsoil,rock,or artificial hard material | m³ | 32.55 |  | 0
E533 | Rock | m³ | 1.4 |  | 0
Filling
Structures
Filling to Structures by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 12.25 |  | 0
E617 | Imported rock of size and grading as specified; include sand blinding on top | m³ | 16.8 |  | 0
Landscaping
E830 | Turfing for lawns around toilet block; include filling with excavated topsoil and the preparation of the surfaces | m² | 73.5 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F122 | 20mm aggregate | m³ | 1.26 |  | 0
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F132 | 20mm aggregate | m³ | 16.31 |  | 0
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F142 | 10mm aggregate | m³ | 16.31 |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, for footings, grade C15, of the following thickness
F611 | Thickness not exceeding 150mm | m³ | 1.26 |  | 0
Bases, Footings and Ground Slabs
Placing mass concrete C20, for ground slab and ramp base of the following thickness
F622 | Thickness 150-300mm | m³ | 9.87 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete C25, for footings of the following thickness
F722 | Thickness 150-300mm | m³ | 4.83 |  | 0
Carried to Collection |  |  |  |  | 0
Beams
F762 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.61 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
G214 | Width 0.4 - 1.22m | m² | 3.5 |  | 0
Fair Finish Plane Vertical
G244 | Width 0.4 - 1.22m | m² | 74.2 |  | 0
Reinforcement
Deformed High Yield Steel
High yield ribbed bars to BS 4449 and of the following sizes
G524 | Nominal size, 6-16mm | t | 0.448 |  | 0
Steel Fabric
Steel fabric reinforcement to BS4483, fabric reference A142, in concrete floor slab with minimum 200mm end side laps, and of the following mass
G563 | Nominal mass 2-3 kg/m² | m² | 60.9 |  | 0
Concrete Accessories
Finishing of top surfaces
Finishing of top surfaces by the following methods
G811 | Class U3 steel trowel finish | m² | 60.9 |  | 0
G812 | Class U2 wood float finish to top of floor of toilet | m² | 5.25 |  | 0
BRICKWORK, BLOCKWORK AND MASONRY
Burnt Clay Brickwork
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.1 | 230 mm thick | m² | 64.4 |  | 0
Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, and of the following thicknesses
U511.2 | 150 mm thick | m² | 83.3 |  | 0
Burnt clay pompei grill brickwork vents, jointed with ordinary 1:4 cement mortar, hoop irons every three courses, as detailed in the drawings of the following sizes
U511.3 | 100 mm thick | m² | 9.1 |  | 0
Damp proof course of bitumen impregnated fabric to BS 6398 for the following wall thickness
U582 | 200 mm thick | m | 74.2 |  | 0
Carried to Collection |  |  |  |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat as specified
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 7 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V333 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 42 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation and undercoat as specified
V553 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 196 |  | 0
WATER PROOFING
Damp Proofing
Rendering
W153 | Rendering of wall surfaces to walls inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar finished with a wood float | m² | 238 |  | 0
Ceramic Tiles
W173 | White ceramic wall tiles to internal faces of walls | m² | 9.8 |  | 0
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid to the surface of sand blinded hardcore fill
W421 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 60.9 |  | 0
Terrazzo floor finish
W441 | 'Surfaces of floors, skirtings and splash aprons | m² | 60.9 |  | 0
MISCELLANEOUS WORKS
Structural
Windows
Supply and fix the following mild steel windows toetails constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, stays, plugging and fixing to wall
X599.1 | Top hung double leaf hinged windows overall size 2000 x 1000mm high comprising of 3mm thick mild steel panes welded on a 25x25x3mm thick angle frame painted colour blue | nr | 2 |  | 0
Carried to Collection |  |  |  |  | 0
Doors
Supply and fix approved solid hardwood doors with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
X599.2 | Single leaf door overall size 800mm x 2100mm (W x H) | nr | 6 |  | 0
X599.3 | 800mm x 2100mm (W x H) split into equal bottom and top leafs each leaf with respective iron mongery, locking and wall stay arrangements | nr | 2 |  | 0
X599.4 | Double leaf door overall size 1750mm x 2100mm (W x H) | nr | 2 |  | 0
Supply and fix the following mild steel grill doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery and accessories
X599.5 | Single leaf door overall size 1000 x 2100mm high | nr | 2 |  | 0
Roofing
X599.6 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board, metal lathe ceiling and eaves, and all roofing timber, gauge 28 blue prepainted GCI sheeting and ridges to the Engineer's satisfaction. | m² | 80.5 |  | 0
Building Finishes
X599.7 | Supply and fix a 450 x 800mm granite "Project Label Plate" to detail as directed by the Engineer | sum | 1 |  | 0
X599.8 | Supply ND 25mm GI pipe toilet grab rail for the disabled toilet complete with all fittings and ancillaries including anchoring into the floor and wall to the Engineers approval and details | nr | 4 |  | 0
X599.9 | Building finishes including; constructing 20x100mm high 1:3 cement-sand skirting, 700mm wide C20 concrete splash apron; supply and installation of 10no. toilet paper holders, installation of floor drains with associated pipework and fitting s connected to soak pit, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
X599.10 | Supply and install 1 no. wooden worktop 1800x400x20mm thick and 3 no. wooden shelves 4000x600x20mm thick made from solid hard wood timber and finished with formica or medium density fibre boards (MDF), include beading, brackets, support structures; complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Water and Drainage
X599.11 | Supply and erect 2000 litre (2m3) high level and 500 litre low level Polyethylene tanks as Polytank, elevated from 2m up to 4m above ground level on a mild steel 80mm steel sectional painted tower or equivalent, complete with access ladders and platforms, including all PN 10 GI/PPR pipework, fittings, gate valves, ball float valve, rain water gutters to low level tank and connection to all water closets, urinal and hand washing facilities in toilet block | sum | 1 |  | 0
X599.12 | Supply materials and install service line connection including all all PN 10 GI/PPR/HDPE plumbing pipe work, fittings and ancillaries from the distribution main to the overhead water tank | sum | 1 |  | 0
X599.13 | Construct Urinal facility with perforated DN 20 PPR/GI water pipework, valves, fittings, floor trap, domical removable cast iron grating, gulley trap | sum | 1 |  | 0
Carried to Collection |  |  |  |  | 0
X599.14 | Provide materials and construct a hand washing facility complete with wash hand basins, DN 13/20 GI/PPR plumbing pipework, uPVC drainage pipework, all fittings, gulley and bottle traps, valves, 13mm diameter chromium plated pillar taps, waste outlet gratings, all accessories, including single low level wash hand basin for disabled person's usage; as per specifications and drawings and to the Engineer's approval | nr | 2 |  | 0
X599.15 | Excavate and construct standard manholes in 200mm thick blockwork, internal depth not exceeding 1.0m, bonded in concrete mortar(1:5) and rendered internally with concrete mortar (1:4), concrete benching, complete with and including CI frame and cover, and interconnecting OD 110mm pvc drain pipes to toilet block | nr | 2 |  | 0
X599.16 | Supply and Install OD 110 mm uPVC PN 6 drainage pipework to BS 4660, complete with spigot and socket joints, all fittings; from toilet block to Septic Tank and Soak Pit | m | 40 |  | 0
X599.17 | Excavate and construct Septic Tank of effective capacity 18m3 in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty cast iron manhole covers | Sum | 1 |  | 0
X599.18 | Excavate and construct 1500mm top/bottom diameter x 2.0m deep soak pit complete including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet | nr | 1 |  | 0
X599.19 | Supply and install squatting type low level water closet suite complete with WC pan, heavy duty cistern complete with anti-vandal cage, flush pipe, connected to nearest manhole; all to the Engineer's satisfaction | nr | 6 |  | 0
X599.20 | Supply and install seat type low level water closet suite complete with WC pan, heavy duty cistern, flush pipe complete with anti-vandal cage, connected to nearest manhole; all to the Engineer's satisfaction | nr | 2 |  | 0
PROVISIONAL SUMS
Electrical Installation
X599.21 | Allow for electric power connection to the toilet block including processing a customer account with UMEME | sum | Rate Only |  | 0
X599.22 | Supply and Install all respective electricals for building lighting; i.e. MCB, metal clad switches, lights, 3core XLPE/SWA/PVC Copper cables, concealed conduits, lights, earthing protection,etc, complete with all accessories as specified and directed by the Engineer | sum | Rate Only |  | 0
X599.23 | Allow for profits and overheads on Item No. Electrical Installation | % | Rate Only |  | 0
Carried to Summary |  |  |  |  | 0
Summary Page
| Page 1 of 7 |  |  |  | 0
| Page 2 of 7 |  |  |  | 0
| Page 3 of 7 |  |  |  | 0
| Page 4 of 7 |  |  |  | 0
| Page 5 of 7 |  |  |  | 0
| Page 6 of 7 |  |  |  | 0
Public Sanitation Waterborne Toilet
Carried to Grand Summary |  |  |  |  | 0

## Bill 7.0 ESS
MINISTRY OF WATER AND ENVIRONMENT
LOT 4 CONSTRUCTION OF ENYAU (MVEPI1&2, OMBECI AND ARIWA) WATER SUPPLY & SANITATION SYSTEM
CONTRACT No. MWE/ WRKS/ …......
BILL No. 7: ENVIRONMENT AND SOCIAL SAFEGUARD MEASURES
Item Nr. | Description | Unit | Quantity | Rate (USh) | Amount (USh)
The works under this bill are covered under the Particular Specifications.
General Provision
7.1 | Sensitise all Contractors staffing, including foremen, supervisors and labourers on the requirement for and full implementation of the ESMP. | Sum | 1 |  | 0
7.2 | Provide for hoarding off construction sites for project infrastructure to intercept any eroded material and any soil material to remain within the site until it is taken away for proper disposal or used for backfilling to avoid loose soil being washed away by storm water. | Sum | 1 |  | 0
7.3 | Ensure no employee is exposed to a noise level greater than 85 dB (A) for a duration of more than 8 hours per day without hearing protection. (National Environment (Noise) Standards and Regulations). Workers operating equipment generating noise levels greater than 80 dBA over long hours must be given earmuffs; | Sum | 1 |  | 0
7.4 | Construct a drainage system with silt traps to reduce impacts of storm water from the construction site | Sum | 1 |  | 0
7.5 | Provide for installation of appropriate sanitary facilities at the campsite and ensure working gangs are provided with mobile toilets that will be maintained and emptied on time. The emptied sanitary waste shall be disposed of at regional feacal sludge treatment Plant. | Sum | 1 |  | 0
7.6 | Develop and implement a Waste Management Plan that puts into consideration sorting at the source, proper storage and transportation. That will at minimum contain the types, nature and quantities of wastes expected to be generated as well as their corresponding methods of treatment and disposal. The plan shall also indicate the sites of proposal as well as the frequency of collection and disposal. | Sum | 1 |  | 0
7.7 | Collect all sorts of waste generated during construction such as HPDE and uPVC offcuts and other accessories associated with water and sanitation projects and handover to recycling facilities. Other forms of waste which are inert or ceramic in nature may be collected by NEMA gazetted waste handlers (Who shall be engaged by the Contractor) and taken to a NEMA gazetted waste disposal facilities for disposal. | Sum | 1 |  | 0
7.8 | Collect and transport all organic waste generated at eating places during construction such as food stuffs to designated Town Council landfills for disposal. | Sum | 1 |  | 0
7.9 | Orient and sensitise all construction workers about responsible sexual behaviour, prevention of Gender Based Violence (GBV) and Sexual Exploitation and Abuse (SEA) in project communities. | Sum | 1 |  | 0
7.1 | Sensitise workers on their sexual rights. The client shall Work with the contractor on establishing zero tolerance policies and codes of conduct related to violence against women and girls (VAWG). | Sum | 1 |  | 0
7.11 | Develop a Health and Safety Policy and Action Plan, addressing workers’ occupational health and safety issues, workers’ welfare and working conditions in line with the Occupational Health and Safety Act of 2006, and World Bank Group EHS general Guidelines, and the EHS guidelines for water projects | Sum | 1 |  | 0
7.12 | Ensure adequate provision of PPEs (gloves, safety shoes, safety belts, overalls and goggles), as well as continuous awareness on the need for use of PPEs and enforcement of usage | Sum | 1 |  | 0
7.13 | Provide First aid facilities on site which are accessible to all personnel. It should among others contain rubber gloves, bandages, pain killers and cotton wool to cater for minor accident victim. | Sum | 1 |  | 0
7.14 | Contractor to have in place a Labour Force Management Plan, in line with the Labour Act and OHS Act. Labour Force Management Plan should address issues of workers’ welfare, child labour, workers code of conduct, sexual harassment among workers, compensation in cases of accidents, payments and contracts, a grievance management mechanism | Sum | 1 |  | 0
7.15 | Contractor to have in place a workers’ code of conduct to address abuse of women and girls that may lead to broken marriages, early pregnancies, sexual exploitation, spread of HIV/AIDS and all kinds of risky and inappropriate behaviour | Sum | 1 |  | 0
7.16 | Ensure works across wetland and streams are undertaken with minimal siltation and transportation of loose soil materials. | Sum | 1 |  | 0
Carried to Summary |  |  |  |  | 0